## COVER
NATIONAL AGENCY FOR THE CONTROL OF AIDS (NACA) WITH FUNDING FROM GLOBAL FUND
RENOVATION AND UPGRADE OF SELECTED PUBLIC HEALTH LABORATORIES IN THE SIX GEOPOLITICAL ZONES IN NIGERIA AND THE NATIONAL EXTERNAL QUALITY ASSESSMENT LABORATORY (NEQAL) UNDER THE GLOBAL FUND RESILIENT & SUSTAINABLE SYSTEMS FOR HEALTH [RSSH] II PROJECT GRANT
LOT 4
PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LABORATORY AT KUBWA GENERAL HOSPITAL, FCT - ABUJA
BILL OF QUANTITIES
JANUARY, 2022

## PRELIMS PCR LAB
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT (N:K)
BILL No 1: PRELIMINARIES
A | Drawings
B | Setting Out
C | Site accomodation for contractor/Storage
D | Water for works
E | Watching and Lighting
F | Security for the works
G | Welfare and Safety
H | First Aid Box
J | Scaffolding
K | Progress Photographs
L | Records
M | Foreman on Site
N | Sign and notice Board
O | Protection for the Works
P | Plant, tools and equipment
Q | Site accomodation for employer representative
R | Clearing / Cleaning
S | Contract Administration
BILL NO 1: PRELIMINARIES CARRIED TO
| GENERAL SUMMARY-: |  |  |  | 0

## KUBWA LAB
BILL OF QUANTITIES FOR THE PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LABORATORY AT KUBWA GENERAL HOSPITAL, FCT - ABUJA
BILL Nr: 2:- LABORATORY
(All provisional)
DEMOLITION AND ALTERATION WORKS
C90: ALTERATIONS-SPOT ITEMS
ROOF
A | Carefully unfix Aluminium roof covering complete with
assoiated works to receive new works as may be directed
by the supervising officers.
| Keep safe materials on site | 362 | Sq.m |  | 0
Removing Finishings
| Wall |  |  |  |  | #REF!
B | Demolish 225mm thick hollow block wall to allow for expansion | 24 | Sq.m |  | 0
C | Carefully hack out ceramic wall complete with weak backing to for new works as may be directed | 5 | Sq.m |  | 0
D | Hack out 13mm thick weak rendering on walls/crack lines
Approximately 25m2
| Remove debris from site | 25 | Sq.m |  | 0
E | Scrape off paeled painting on surfaces of rendered walls | 15 | Sq.m |  | 0
Ceiling
F | Remove existing but damaged/nonstandard ceiling finishing
complete with weak/damaged noggins
Approximately 66m2
| Keep safe materials on site | 66 | Sq.m |  | 0
Floor
G | Hack - off existing but damaged floor tiles complete with
asoociated screeding
Approximately 52m2
| Remove debris from site | 52 | Sq.m |  | 0
Doors.
H | Carefully Un-fix sub-standard flush/metal door complete with frame to allow for new works in opening
| Size 1200 x 2100mm high | 1 | Nr. |  | 0
J | Dtto, 900 x 2100mm high | 3 | Nr. |  | 0
K | Dtto, 750 x 2100mm high | 2 | Nr. |  | 0
L | Allow a sum for making good all disturbed finishings
| during demolition | 1 | Sum |  | 0
| To Collection |  |  |  | 0
A | Carefully unfix existing worktops tops complete with drawers and other compactments to allow for reconstruction as may be directed by the supervisor |  |  |  | 0
Mechanical Fittings
B | Carefully remove damaged and substandard basin and taps | 2 | Nr. |  | 0
C | Carefully remove existing but damaged flexible connector | 4 | Nr. |  | 0
D | Carefully remove damaged Water closet complete | 2 | Nr. |  | 0
E | Carefully remove damaged wash hand basin complete | 2 | Nr. |  | 0
F | Carefully uninstall eixsting but damaged/faulty Airconditioners of various sizes to allow for new installations/repairs
| Keep safe materials on site | 2 | Nr. |  | 0
Electrical Fittings
G | Carefully remove damaged ceiling mounted lighting
| fittings complete | 12 | Nr. |  | 0
H | Carefully remove existing wall mounted lighting
| fittings complete | 2 | Nr. |  | 0
J | Carefully remove damaged wall mounted
| security lighting fittings | 2 | Nr. |  | 0
K | Carefully remove damaged sockets of various sizes | 12 | Nr. |  | 0
L | Allow for the pulling out and replacement of damaged cables of various sizes | 1 | Sum |  | 0
| To Collection:- |  |  |  | 0
COLLECTION
| Page 1 |  |  |  | 0
| Page 2 |  |  |  | 0
DEMOLITION AND ALTERATION WORKS
| carried to summary |  |  |  | 0
NEW WORKS
ELEMENT Nr. 1: WORK BELOW
THE GROUND FLOOR BED (Provisional)
D20: EXCAVATING AND FILLING
Site Preparation
A | Clearing site vegetation;
| Shrubs and bushes and grub their roots | 70 | Sq.m |  | 0
Removing trees
B | Girth 1500 -3000mm | 2 | Nr. |  | 0
Excavating
C | Top soil for preservation;
| Average depth 150mm | 12 | m2 |  | 0
D | Trenches width > 0.3m
| Maximum depth < 2.00m | 49 | Cu.m |  | 0
E | Pits
| Maximum depth < 2.00m | 6 | Cu.m |  | 0
Disposal
F | Excavated material;
Offsite:
| 2km away from the site | 30 | Cu.m |  | 0
Filling to make up levels
G | Average thickness >0.25m;
arising from the excavations;
Selected laterite in layers exceeding
| 250mm | 25 | Cu.m |  | 0
H | Average thickness < 0.25m;
Laterite obtained off site
| Selected in layers not exceeding 150mm | 33 | Cu.m |  | 0
J | Average thickness > 0.25m;
Hardcore obtained off site;
| handpacked | 22 | Cu.m |  | 0
K | Average thicknes < 0.25m;
Fine sand obtained off site
| Blinded over hardcore surfaces | 74 | Sq.m |  | 0
L | Damp proof membrane laid on blinded surface of hardcore | 74 | Sq.m |  | 0
Surface treatments
M | Applying 'Dieldrex' pesticides to surface of
| excavation | 183 | Sq.m |  | 0
| To Collection |  |  |  | 0
E05: IN SITU CONCRETE CONSTRUCTION
GENERALLY
In situ concrete (1:3:6 - 36mm aggregate to attain minimum works
strength of 25N/mm2 in 28 days and poured at a height not more
than 3.00m
A | Foundations
Poured on or against earth or unblended
| hardcore | 8 | Cu.m |  | 0
In situ concrete (1:2:4 - 19mm aggregate) to
attain minimum works strength of 25N/mm2 in 28
days and poured at a height not more than 3.00m
B | Beds
Poured on or against earth or unblended
| hardcore | 11 | Cu.m |  | 0
C | Column Bases/Columns
Poured on or against earth or unblended
| hardcore | 2 | Cu.m |  | 0
E20: FORMWORK FOR IN SITU CONCRETE
Sawn formwork
D | Sides of foundation
plain vertical
| Height < 250mm | 24 | Lin.m |  | 0
E | Sides of foundation
plain vertical
| Height 250-500mm | 5 | Sq.m |  | 0
Columns
Isolated
F | Rectangular shape 225 X 225mm | 9 | Sq.m |  | 0
E30: REINFORCEMENT FOR IN SITU CONCRETE
High tensile reinforcement bars
Bar
G | 10 - 16mm diameter
| Bent | 0.12 | Tones |  | 0
H | 10mm diameter
| Link | 0.05 | Tones |  | 0
J | Fabric
| Ref. A193 weight 29kg/m2 | 73 | Sq.m |  | 0
| To Collections |  |  |  | 0
F10: BRICK/BLOCK WALLING
Hollow sandcrete blockwall bedded and jointed
in cement mortar (1:6) and laid in stretcher bond
and filled solid with concrete (1:3:6 - 36mm
aggregate)
A | Walls
230mm thick
| Vertical | 86 | Sq.m |  | 0
B | Walls
150mm thick
| Vertical | 7 | Sq.m |  | 0
M20: PLASTERED/RENDERED/ROUGHCAST
COATINGS
EXTERNAL
Cement and sand (1:4) smooth rendering
C | Walls
Width >300mm
| 12mm thck | 12 | Sq.m |  | 0
M60: PAINTING/CLEAR FINISHINGS
Prepare, prime and apply one undercoat and
two finishing coats of 'Berger' or other equal
and approved high quality emulsion paint on rendered face of wall
D | General Surfaces
| Girth > 300mm | 12 | Sq.m |  | 0
| To Collections |  |  |  | 0
COLLECTION
| Page 3 |  |  |  | 0
| Page 4 |  |  |  | 0
| Page 5 |  |  |  | 0
WORK BELOW THE GROUND FLOOR BED
| carried to summary;- |  |  |  | 0
EXTERNAL AND INTERNAL WALL
E05: IN SITU CONCRETE CONSTRUCTION
GENERALLY
In situ concrete (1:2:4 - 19mm aggregate) to
attain minimum works strength of 25N/mm2 in 28
days and poured at a height not more than 3.00m
A | Lintels
Isolated
| Reinforced | 2 | Cu.m |  | 0
B | Column
Isolated
| Reinforced | 1 | Cu.m |  | 0
E20: FORMWORK FOR IN SITU CONCRETE
Sawn formwork
C | Lintels
Attached to walls
| Rectangular 225 X 225mm | 37 | Sq.m |  | 0
D | Column
Attached to walls
| Rectangular 225 X 225mm | 9 | Sq.m |  | 0
E30: REINFORCEMENT FOR IN SITU CONCRETE
High tensile reinforcement bars
Bar
E | 10 - 16mm diameter
| Bent | 0.04 | Tones |  | 0
F | 10mm diameter
| Links | 0.02 | Tones |  | 0
F10: BRICK/CEMENT BLOCK WALLING
Hollow sandcrete blockwall laid in stretcher bond
bedded and jointed in cement mortar (1:6)
Walls
G | 225mm thick
| vertical | 201 | Sq.m |  | 0
H | 150mm thick
| vertical | 15 | Sq.m |  | 0
EXTERNAL AND INTERNAL WALL
| carried to summary |  |  |  | 0
ROOF CONSTRUCTION
AND COVERING
E05: IN SITU CONCRETE CONSTRUCTION
GENERALLY
In situ concrete (1:2:4 - 19mm aggregate) to attain
minimum works strength of 25N/mm2 in 28days
and poured at a height not more than 3.00m
Beams
A | Isolated
| Reinforced | 1 | Cu.m |  | 0
B | Fascia | 2 | Cu.m |  | 0
E20: FORMWORK FOR IN SITU CONCRETE
Sawn formwork
Beams
C | Attached to walls
| Rectangular 225 X 225mm | 20 | Sq.m |  | 0
D | Ditto, Concrete fascia | 23 | Sq.m |  | 0
E30: REINFORCEMENT FOR IN SITU CONCRETE
High tensile reinforcement bars
Bar
E | 10 - 16mm diameter
| Straight | 0.39 | Tones |  | 0
F | 10mm diameter
| Links | 0.09 | Tones |  | 0
G20: CARPENTRY/TIMBER FRAMING/FIRST FIXING
Sawn Hardwood treated with preservatives
Roof Members
Pitched
G | 50 X 150mm | 565 | Lin.m |  | 0
H | 50 X 100mm | 485 | Lin.m |  | 0
J | 50 X 75mm ditto | 618 | Lin.m |  | 0
K | 50 X 50mm | 395 | Lin.m |  | 0
| Carried to collection:- |  |  |  | 0
H31: METAL PROFILED SHEET CLADDING/
COVERING/SIDING
Queen Aluminium' or other equal and approved
0.55mm guage corrugated coloured longspan aluminium roofing
sheet with one and half corrugation side laps nailed to timber
purlins with and including matching nails (measured nett - no
allowance made for laps)
A | Roof Coverings
| Pitch 200 from horizontal | 418 | Sq.m |  | 0
B | Eaves
| 200mm girth | 72 | Lin.m |  | 0
C | Ridges/hip
| 600mm girth | 52 | Lin.m |  | 0
| To collections |  |  |  | 0
COLLECTION
| Page 7 |  |  |  | 0
| Page 8 |  |  |  | 0
ROOF CONSTRUCTION
| carried to summary;- |  |  |  | 0
WINDOWS
Chartered Aluminium' or other equal approved
Colour; powder coated standard gauge aluminium
casement windows factory glazed with
6mm thick plain glass; with a combined fixed and
sliding insect screen to Architect specification;
complete with all accessories and ironmongery
including pinning and lugging and bedding in cement
mortar (1:6) to concrete or blockwork
Casement windows and window frames
A | Size 1200 X 1200mm high | 7 | Nr |  | 0
B | Size 1000 X 1200mm high | 2 | Nr |  | 0
C | Size 600 X 600mm high | 4 | Nr |  | 0
BURGULAR PROOF
16mm wrot iron bars welded at joint according
to Architect's instruction horizontally at 150mm centres
and vertical at 300mm centres, including pinning, lugging
and bedding in block work or concrete work
D | Size 1200 X 1200mm high | 7 | Nr |  | 0 |  | 18000
E | Size 1000 X 1200mm high | 2 | Nr |  | 0
F | Size 600 X 600mm high | 4 | Nr |  | 0
| WINDOWS |  |  |  | 0
carried to summary
DOORS
DOORS/SHUTTERS/HATCHES
STEEL
Supply and install approved high quality 44mm thick steel Flush doors complete with 50mm thick full jamb frame, sub frame, architrave and Ironmongery including observer view glass bay
Door size
A | 1200 x 2050mm high | 1 | Nr. |  | 0
44mm thick high quality and approved American steel door complete
with associated frame, ironmongery and other assesories, fixed in
compliance to the manufacture's printed manuals and as ma be
directed by the project supervisor
B | 900 x 2050mm high | 4 | Nr. |  | 0
C | 750 x 2050mm high | 4 | Nr. |  | 0
D | Supply and install approved authomatic door closer | 2 | Nr. |  | 0
| DOORS CARRIED TO SUMMARY |  |  |  | 0
FITTINGS AND FIXTURES
A | Provide, fabrication and installation of an "L" shape (HDF) laboratory work tops comprising: drawers leg spaces and store shelves finished in epoxy resin or seamless granite work surface Size 750mm wide x 900mm high | 8 | Lin.m |  | 0
B | Work Station highlander size 750 x 1200mm x 900mm high | 1 | Nr |  | 0
N FURNITURE/EQUIPMENT
| Carried to Summary |  |  |  | 0
WALL FINISHING
INTERNALLY
M20: PLASTERED/RENDERED/ROUGHCAST
COATINGS
Cement and sand (1:4) rendering
Walls
A | Width > 300mm
| 13mm thick | 230 | Sq.m |  | 0
Wall Screeding
B | Prepare and apply POP screeded finish on rendered wall | 120 | Sq.m |  | 0
M60: PAINTING/CLEAR FINISHINGS
Prepare and apply one undercoat and two finishing coat
of MAYER paint or other equal and approved high quality
satin paint on screeded wall.
General Surfaces
D | Girth > 300mm | 120 | Sq.m |  | 0
E | Width < 300mm | 98 | Lin.m |  | 0
EXTERNALLY
M60: PAINTING/CLEAR FINISHINGS
Prepare and apply one undercoat and two finishing coat
of Berger paint or other equal and approved high quality
emulsion paint on rendered wall.
General Surfaces
G | Girth > 300mm | 233 | Sq.m |  | 0
0
H | Width < 300mm | 58 | Lin.m |  | 0
0
J | Fascia board, Girth > 300mm | 58 | Sq.m |  | 0
WALL FINISHING
| CARRIED TO SUMMARY;- |  |  |  | 0
FLOOR FINISH
M10: CEMENT: SAND/CONCRETE SCREEDS/TOPPINGS
Cement and sand (1:4) screeded bed 40mm thick to receive
floor tilling
A | Floors
| Levels or to falls only < 150 from horizontal | 76 | Sq.m |  | 0
B | Skirting
| 100mm high | 112 | Lin. M |  | 0
M40: STONE/CONCRETE/QUARRY/CERAMIC
TILING/MOSAIC
Epoxy Floor Finish
E | Blinding steel surface 50 thick | 2 | Sq.m |  | 0
General floor surface preparation
F | Surface Preparation; Floor shall be acid washed, so that all
contermination in the floor is completely cleaned and ready for
| to receive epoxy finishes. | 52 | Sq.m |  | 0
Epoxy Finish
Apply Epoxy Primer Nitoprime 25, manufactured by Fosroc,
applied on a prepared surface and antislip grains spread over
the same to ensure mechanical key with the subsequent
epoxy treatment. Nitoflor TF 5000, chemical and abrasion
resistant epoxy floor screed, manufactured by Fosroc,
shall then be laid by skill workers @ 3mm thickness on the
Primer Nitoprime 25 as per manufacturer's specification.
The screed shall have a conpressive strength of
85N / sqmm and Flexural strength of 28 N / sqmm
Nitroflor TF 5000 is resistant to Acids, Alkalis, Solvents &
Organics and Aqueous solutions. The screed shall thereafter be
sealed with Nitoflor SL2000, chemical & abrasion resistant
epoxy floor topping manufactured by Fosroc. Nitoflor SL2000
shall be trowel finished to give a smooth finish with 5mm overall
thickness.
G | Epoxy flooring system Internally | 52 | Sq.m |  | 0
FLOOR FINISHINGS
| CARRIED TO SUMMARY;- |  |  |  | 0
CEILING FINISHINGS
INTERNAL / EXTERNAL
M20 PLASTERED/RENDERED/ROUGHCAST
COATINGS
M31: FIBROUS PLASTER
In situ cast plaster of paris suspended ceiling slabs cast
to Architect's design including all necessary accessories and
fixing to sofit of concrete floor slab or hardwood noggings (m/s)
A | Ceiling
Width > 300mm
5mm thick
| pannelled slab | 129 | Sq.m |  | 0
Prepare, prime and apply one undercoat and two finishing
coats of Satin paint of Mayer, Berger or other equal and
approved to soffit of ceiling
B | Ceiling soffit
| Width > 300mm | 129 | Sq.m |  | 0
CEILING FINISHINGS
| carried to summary |  |  |  | 0
SANITARY APPLIANCES/FITTINGS
Fittings, equipment and appliances associated
with services.
A | Twyford or equal approved low level water closet suite comprising
vitreous china bowl plugged and screwed to tiled
floor (m.s); 8 litre vitreous china tank and cover
complete with 'Union' flushing mechanism plugged
and screwed to wall with and including matching
screws; 'Radof' or other and approved white uPVC
| seat and cover screwed to bowl | 2 | Nr. |  | 0
B | Twyford or other equal and approved wash hand
basin complete with 'Union' or other equal and
approved chrome plated waste; chrome plated
chain and black rubber stay; 'Union' or other equal
and approved UPVC bottle trap; chrome plated
heavy duty bib tap including brackets and plugging
| and screwing brackets to wall | 2 | Nr. |  | 0
D | White vitreous, China recessed soap dish
bedded and jointed with cement and sand
mortar (1:4) to wall including pointing all round
| the edges with white cement | 2 | Nr. |  | 0
E | Pipes
Flexible
600mm long 12mm diameter serated stainless
| steel connector with end bolts | 8 | Nr. |  | 0
F | Heavy gauge steel tap with all necessary fittings | 4 | Nr |  | 0
G | Allow for complete replacement of existing but damaged
supply/waste piping with appropriate UPVC pressure pipe
to be executed complete, including making good all other
| faults as may be directed | 1 | Sum | 0 | 0
H | Supply and install Sensor tap to WHB and Sink complete with all
| accessories | 2 | Nr |  | 0
FIRE FIGHTING SYSTEM /DETECTORS
J | Suplly and fix in place DCP ABC - 9Kg Fire Extinguisher | 2 | Nr |  | 0
SANITARY APPLIANCES/FITTINGS
| CARRIED TO SUMMARY;- |  |  |  | 0
ELECTRICAL INSTALLATIONS
Y61: HV/LV CABLES AND WIRING
Kabel Metal or NOCACO copper cable 450/700V
grade PVC insulated and colour coded to B.S.
6004 Table 1A copper cable; Nigerpipe heavy
gauge UPVC conduit pipe
Cables and conduit in final circuits
2Nr. 1.5mm2 1 - core cable drawn into 20mm
pipe in radial main sub - circuit
A | Lighting outlets | 12 | Nr |  | 0
B | One way switches | 5 | Nr |  | 0
C | Two way switches | 2 | Nr |  | 0
D | 3Nr. 2.5mm2 1 - core cable drawn into 20mm
pipe in ring main sub circuit
| Sockets, switch sockets and the like | 4 | Nr |  | 0
E | 3Nr. 4mm2 1 - core cable drawn into 20mm
pipe in ring main sub circuit
| Sockets, switch sockets and the like | 2 | Nr |  | 0
Y73: LUMINAIRES AND LAMPS
Philips or other equal and approved, complete
with conduit boxes patteraes, ceiling roses,
connector blocks, flexible cords, starters, chokes
capacitors, shades, diffusers, reflectors etc
Luminaires
F | Ceiling mounted fittings complete with energy saving bulb
plugged and screwed to concrete soffits.
| 45w | 38 | Nr |  | 0
G | 1 x 100W Bulk head wall mounted security
lighting fittings plugged and screwed to wall
| 100w | 4 | Nr. |  | 0
Y74: ACCESSORIES FOR ELECTRICAL SERVICES
ABB series single pole flush mounted shuttered
white plastic fronted plate lighting switches
mounted with galvanised mild steel knock out box
fitted with brass earth terminal complete with
fitting and accessories
Accessories
H | 5A; 1 - gang 1 - way flush mounted
| Concrete or blockwall background | 8 | Nr |  | 0
J | 5A; 1 - gang 2 - way flush mounted
| Concrete or blockwall background | 1 | Nr |  | 0
| To Collection:- |  |  |  | 0
ABB series single pole flush mounted shuttered
white plastic fronted plate lighting switches
mounted with galvanised mild steel knock out box
fitted with brass earth terminal complete with
fitting and accessories
Accessories
A | 13A; 1 - gang flush mounted metal clad switched
socket outlet plugged and screwed
| Concrete or blockwall background | 3 | Nr |  | 0
B | 13A; (Twin) flush mounted metal clad switched
socket outlet plugged and screwed
| Concrete or blockwall background | 6 | Nr |  | 0
C | 15A; 1 - gang flush mounted switched socket
outlet plugged and screwed
| Concrete or blockwall background | 3 | Nr |  | 0
D | 15A; (Twin) flush mounted switched socket
outlet plugged and screwed
| Concrete or blockwall background | 1 | Nr |  | 0
| To Collection:- |  |  |  | 0
COLLECTION
| Page 16 |  |  |  | 0
| Page 17 |  |  |  | 0
ELECTRICAL INSTALLATION
| carried to summary |  |  |  | 0
EXTERNAL WORKS
MECHANICAL WORKS
A | Allow the provision of N1,350,000.00 for the construction of 6m high steel stantion complete with 1No 3000litres GP overhead tank including all structural works, installations works and reticulation and maybe directed by the project supervisor | 1 | Sum | 0 | 0
B | Allow the sum of N500,000.00 for complete water reticulations as maybe directed by the project supervisor | 1 | Sum | 0 | 0
C | Carefully unistall and re-install paved walkway complete with kerbs
| and other associated works to allow for expansion of the Lab | 135 | Sq.m |  | 0
Lanterns
D | Supply, install and commission Integrated Solar powered Led Street
lighting lanterns, 160LM/W 150W, All in one light integrated
| panel outdoor high luminaire, with adjustable angle bracket, | 8 | Nr |  | 0
waterproff IP66 with motion sensor, mounted on 6m double arm
galvanised steel pole ref. THORN QG3 welded to base plate well
bedded into a reinforced concreted bases size, Top diamention
550 x 550mm; bottom diamention 850 x 850mm and a depth of
1150mm to receive poles…
EXTERNAL WORKS
| carried to summary;- |  |  |  | 0
SUMMARY
| DEMOLITION WORK |  |  |  | 0
| WORK BELOW THE GROUND FLOOR BED |  |  |  | 0
| EXTERNAL AND INTERNAL WALL |  |  |  | 0
| ROOF |  |  |  | 0
| WINDOWS |  |  |  | 0
| DOORS |  |  |  | 0
| FITTINGS AND FIXTURES |  |  |  | 0
| WALL FINISHINGS |  |  |  | 0
| FLOOR FINISHINGS |  |  |  | 0
| CEILING FINISHINGS |  |  |  | 0
| SANITARY APPLIANCES/FITTINGS |  |  |  | 0
| ELECTRICAL INSTALLATION |  |  |  | 0
| EXTERNAL WORKS |  |  |  | 0
LABORATORY MODIFICATION/UPGRADING
| carried to general summary |  |  |  | 0

## SAMPLE COLLECTION SHADE
RELOCATION OF SAMPLE COLLECTION SHADE
BILL Nr 3;- SAMPLE COLLECTION SHADE
(All provisional)
DEMOLITION AND ALTERATION WORKS
ROOF
A | Carefully unfix Aluminium roof covering complete with
assoiated works to allow for Laboratory expansion
as may be directed by the supervising officers.
Approximately in 45m2
| Keep safe materials on site | 45 | Sq.m |  | 0
STEEL TRUSSESS
B | Carefully unfix steel roof trussess complete to allow for
expansion works as may be directed and Keep safe
| materials on site Approximately in 45m2 | 45 | Sq.m |  | 0
| Wall |  |  |  |  | #REF!
C | Demolish 225mm thick hollow block work shade complete with concrete in foundation, slab and associated finishing to allow for Laboratory expansion | 32 | Sq.m |  | 0
Approximately in 32m2
Ceiling
H | Carefully unfix existing ceiling finishing complete with
associated works and noggins and keep safe materials
| on site (Approximately 32m2) | 32 | Sq.m |  | 0
Electrical Fittings
M | Carefully un-fix ceiling mounted lighting fittings
| complete fittings complete | 8 | Nr. |  | 0
P | Carefully remove 13A sockets | 2 | Nr. |  | 0
DEMOLITION AND ALTERATION WORKS
| carried to summary |  |  |  | 0
NEW WORKS
ELEMENT Nr. 1: WORK BELOW
THE GROUND FLOOR BED (Provisional)
D20: EXCAVATING AND FILLING
Site Preparation
A | Clearing site vegetation;
| Shrubs and bushes and grub their roots | 28 | Sq.m |  | 0
Excavating
B | Top soil for preservation; Average depth 150mm | 28 | Sq.m |  | 0
C | Trenches width > 0.3m and maximum depth < 2.00m | 21 | Cu.m |  | 0
D | Pits; Maximum depth < 2.00m | 3 | Cu.m |  | 0
Filling to make up levels
E | Average thickness >0.25m;
arising from the excavations;
| Selected laterite in layers exceeding 250mm | 14 | Cu.m |  | 0
F | Average thickness < 0.25m;
Laterite obtained off site
| Selected in layers not exceeding 150mm | 10 | Cu.m |  | 0
G | Average thickness > 0.25m;
| Hardcore obtained off site; handpacked | 8 | Cu.m |  | 0
H | Average thicknes < 0.25m;
Fine sand obtained off site
| Blinded over hardcore surfaces | 8 | Sq.m |  | 0
J | Damp proof membrane laid on blinded surface of hardcore | 40 | Sq.m |  | 0
Surface treatments
K | Applying 'Dieldrex' pesticides to surface of
| excavation | 56 | Sq.m |  | 0
E05: IN SITU CONCRETE CONSTRUCTION
GENERALLY
In situ concrete (1:3:6 - 36mm aggregate to
attain minimum works strength of 25N/mm2 in 28
days and poured at a height not more than 3.00m
L | Foundations; Poured on or against earth or unblended
| hardcore | 3 | Cu.m |  | 0
| To Collection |  |  |  | 0
In situ concrete (1:2:4 - 19mm aggregate) to
attain minimum works strength of 25N/mm2 in 28
days and poured at a height not more than 3.00m
A | Beds; Poured on or against earth or unblended
| hardcore | 4 | Cu.m |  | 0
B | Block to Receive vertical steel posts | 1 | Cu.m |  | 0
E20: FORMWORK FOR IN SITU CONCRETE
Sawn formwork
C | Sides of foundation
plain vertical
| Height < 250mm | 21 | Lin.m |  | 0
D | Sides of Blocks
plain vertical
| Height > 250mm | 5 | Sq.m |  | 0
E30: REINFORCEMENT FOR IN SITU CONCRETE
High tensile reinforcement bars
E | Fabric
| Ref. A193 weight 29kg/m2 | 40 | Sq.m |  | 0
F10: BRICK/BLOCK WALLING
Hollow sandcrete blockwall bedded and jointed in
cement mortar (1:6) and laid in stretcher bond and filled
solid with concrete (1:3:6 - 36mm aggregate)
F | Walls; 230mm thick; Vertical | 27 | Sq.m |  | 0
M20: PLASTERED/RENDERED/ROUGHCAST
COATINGS
EXTERNAL
Cement and sand (1:4) smooth rendering
G | 12mm thick; Walls; Width >300mm | 10 | Sq.m |  | 0
M60: PAINTING/CLEAR FINISHINGS
Prepare, prime and apply one undercoat and two
finishing coats of 'Berger' or other equal and approved
high quality emulsion paint on rendered face of wall
H | General Surfaces
| Girth > 300mm | 10 | Sq.m |  | 0
| To Collection |  |  |  | 0
COLLECTION
| Page 2 |  |  |  | 0
| Page 3 |  |  |  | 0
WORK BELOW THE GROUND FLOOR BED
| carried to summary;- |  |  |  | 0
ROOF CONSTRUCTION
AND COVERING
Structural Steelwork
Fabricated; weldeable steel; BS 4360; grade 43C, welded fabrication and bolted site connection in accordance with BS 449
A | Steel top and bottom; member; angle size 45 x 45 x 1.2mm thick (3.77kg/m) | 360 | kg |  | 0
B | Steel struts and braces; member; angle size 25 x 25 x 6mm thick (3.32kg/m) | 290 | kg |  | 0
C | Purlins; member; sqauer pipe size 40 x 40 x 1.2mm thick (3.77kg/m) | 352 | kg |  | 0
D | Cladding; member; angle size 25 x 25 x 1.2mm thick (3.32kg/m) | 279 | kg |  | 0
Unframed Steelwork
E | Post; Vertical Hollow stell Circular pipes; members; Steel Diameter 75mm x 2mm thick welded together with roof trusses | 26 | Lin.m |  | 0
F | Base plates; 450 x 280 x 12mm thick mild steel welded to base of Posts | 8 | Nr |  | 0
Fittings, connections, fixings and anchorages
G | 12mm anti-sag rod | 8 | kg |  | 0
H | 20mm diameter hold down bolts; 500mm long; connecting steel post to column/beams (measured separately) | 8 | Nr |  | 0
Painting
Touch up primer and apply two coats of red oxide paint to surfaces of steelwork before erection
J | Steelwork | 45 | m2 |  | 0
H31: METAL PROFILED SHEET CLADDING/
COVERING/SIDING
Corrugated longspan aluminium roof sheeting of approved colour; lapped one corrugation at sides and 150mm at ends; fixed in accordance with manufacturer's instructions to steel purlins (measured separately)
K | Roof Coverings
| Pitch not exceeding 500 from horizontal | 42 | Sq.m |  | 0
L | Eave flashing; 200mm girth | 23 | Lin.m |  | 0
M | Ridges/hip; 600mm girth | 16 | Lin.m |  | 0
ROOF CONSTRUCTION
| carried to summary;- |  |  |  | 0
FLOOR FINISH
M10: CEMENT: SAND/CONCRETE SCREEDS/TOPPINGS
Cement and sand (1:4) screeded bed 40mm thick to
receive floor tilling
A | Floors
| Levels or to falls only < 150 from horizontal | 28 | Sq.m |  | 0
M40: STONE/CONCRETE/QUARRY/CERAMIC
TILING/MOSAIC
OFFICE TILING
600 x 600 x 10mm thick glazed vitrified floor tiles
laid on cement and sand (1:4) screeded
bed and pointed all round the edges with cement
B | Floors
| Levels or to falls only < 150 from horizontal | 28 | Sq.m |  | 0
FLOOR FINISHINGS
| CARRIED TO SUMMARY;- |  |  |  | 0
CEILING FINISHINGS
INTERNAL / EXTERNAL
M20 PLASTERED/RENDERED/ROUGHCAST
COATINGS
13mm thick well seasoned plywood board nailed in place to hardwood noggins (m/s) as Ceiling finishing in compliance to Approved Architect's design/pattern complete with all necessary accessories
A | Ceiling
Width > 300mm
5mm thick
| pannelled slab | 25 | Sq.m |  | 0
CEILING FINISHINGS
| carried to summary |  |  |  | 0
SANITARY APPLIANCES/FITTINGS
Fittings, equipment and appliances associated
with services.
A | Twyford or other equal and approved wash hand
basin complete with 'Union' or other equal and
approved chrome plated waste; chrome plated
chain and black rubber stay; 'Union' or other equal
and approved UPVC bottle trap; chrome plated
heavy duty bib tap including brackets and plugging
| and screwing brackets to wall | 1 | Nr. |  | 0
B | Heavy gauge steel tap with all necessary fittings | 1 | Nr |  | 0
C | Allow the sum of N150,000.00 for the provision and
installation of supply/waste piping with appropriate
UPVC pressure pipe to be executed complete, including
| making good all other faults as may be directed |  | Sum | 0 | 0
D | Supply and install Sensor tap to WHB complete with all
| accessories | 1 | Nr |  | 0
SANITARY APPLIANCES/FITTINGS
| CARRIED TO SUMMARY;- |  |  |  | 0
ELECTRICAL INSTALLATIONS
Y61: HV/LV CABLES AND WIRING
Kabel Metal or NOCACO copper cable 450/700V
grade PVC insulated and colour coded to B.S.
6004 Table 1A copper cable; Nigerpipe heavy
gauge UPVC conduit pipe
Cables and conduit in final circuits
2Nr. 1.5mm2 1 - core cable drawn into 20mm
pipe in radial main sub - circuit
| Lighting outlets | 12 | Nr |  | 0
Y73: LUMINAIRES AND LAMPS
Philips or other equal and approved, complete
with conduit boxes patteraes, ceiling roses,
connector blocks, flexible cords, starters, chokes
capacitors, shades, diffusers, reflectors etc
Luminaires
B | Ceiling mounted fittings complete with energy saving bulb
plugged and screwed to concrete soffits.
| Drop < 1.00m | 12 | Nr |  | 0
ABB series single pole flush mounted shuttered
white plastic fronted plate lighting switches
mounted with galvanised mild steel knock out box
fitted with brass earth terminal complete with
fitting and accessories
Accessories
C | 13A; 1 - gang flush mounted metal clad switched
socket outlet plugged and screwed
| Concrete or blockwall background | 1 | Nr |  | 0
D | 13A; (Twin) flush mounted metal clad switched
socket outlet plugged and screwed
| Concrete or blockwall background | 2 | Nr |  | 0
ELECTRICAL INSTALLATION
| CARRIED TO SUMMARY;- |  |  |  | 0
SUMMARY
| DEMOLITION WORK |  |  |  | 0
| WORK BELOW GROUND LEVEL |  |  |  | 0
| ROOF |  |  |  | 0
| FLOOR FINISHINGS |  |  |  | 0
| CEILING FINISHINGS |  |  |  | 0
| SANITARY APPLIANCES/FITTINGS |  |  |  | 0
| ELECTRICAL INSTALLATION |  |  |  | 0
SAMPLE COLLECTION BAY
| carried to summary |  |  |  | 0

## SUMMARY
GENERAL SUMMARY
BILL Nr. 1 - PRELIMINARIES | 0
BILL Nr. 2 - LABORATORY EXTENTION/MODIFICATIONS | 0
BILL Nr. 3 - SAMPLE COLLECTION SHADE | 0
RENOVATION/UPGRADING OF PCR LAB,
TOTAL ESTIMATE - | 0