## COVER SHEET
NATIONAL AGENCY FOR THE CONTROL OF AIDS (NACA) WITH FUNDING FROM GLOBAL FUND
RENOVATION AND UPGRADE OF SELECTED PUBLIC HEALTH LABORATORIES IN THE SIX GEOPOLITICAL ZONES IN NIGERIA AND THE NATIONAL EXTERNAL QUALITY ASSESSMENT LABORATORY (NEQAL) UNDER THE GLOBAL FUND RESILIENT & SUSTAINABLE SYSTEMS FOR HEALTH [RSSH] II PROJECT GRANT
LOT 1
PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LAB AT DR. LAWRENCE HENSHAW MEMORIAL HOSPITAL CALABAR, CROSS-RIVER STATE
BILL OF QUANTITIES
JANUARY, 2022

## PRELIMINARIES
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT (N:K)
BILL No 1: PRELIMINARIES
A | Drawings
B | Setting Out
C | Site accomodation for contractor/Storage
D | Water for works
E | Watching and Lighting
F | Security for the works
G | Welfare and Safety
H | First Aid Box
J | Scaffolding
K | Progress Photographs
L | Records
M | Foreman on Site
N | Sign and notice Board
O | Protection for the Works
P | Plant, tools and equipment
Q | Site accomodation for employer representative
R | Clearing / Cleaning
S | Contract Administration
BILL NO 1: PRELIMINARIES CARRIED TO
| GENERAL SUMMARY-: |  |  |  | 0

## LABS 2021
BILL OF QUANTITIES FOR THE PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LABS AT DR. LAWRENCE HENSHAW MEMORIAL HOSPITAL CALABAR, CROSS-RIVER STATE
LABORATORY
DEMOLITION AND ALTERATION WORKS
C90: ALTERATIONS-SPOT ITEMS
(All provisional)
Removing Finishings
| Wall |  |  |  | #REF!
A | Carefully cut 225mm thick wall to creat doors as may be directed | 18 | Sq.m | 0
B | Hack out 13mm thick weak rendering on walls/crack
lines; Approximately 9m2
| Remove debris from site | 9 | Sq.m | 0
C | Scrape off paeled painting on surfaces of rendered walls | 566 | Sq.m | 0
Ceiling
D | Remove existing but damaged/nonstandard ceiling
finishing complete with weak/damaged noggins
Approximately 47m2
| Keep safe materials on site | 47 | Sq.m | 0
Floor
E | Hack - off existing but damaged floor tiles complete
with asoociated screeding
| Remove debris from site | 92 | Sq.m | 0
Doors.
F | Carefully Un-fix sub-standard flush/metal door complete with frame to allow for new works in opening
| Size 1500 x 2100mm high | 10 | Nr. | 0
G | Allow a sum for making good all disturbed finishings
during demolition
H | Carefully unfix existing worktops tops complete with drawers and other compactments to allow for reconstruction as may be directed by the supervisor | 1 |  | 0
J | Carefully uninstall eixsting but damaged/faulty Airconditioners of various sizes to allow for new installations/repairs |  | Item | 0
Keep safe materials on site
DEMOLITION AND ALTERATION WORKS
| carried to summary |  |  | 0
NEW WORKS
ELEMENT Nr. 1: WORK BELOW
THE GROUND FLOOR BED (Provisional)
D20: EXCAVATING AND FILLING
Site Preparation
A | Clearing site vegetation;
| Shrubs and bushes and grub their roots | 46 | Sq.m | 0
Excavating
B | Top soil for preservation;
| Average depth 150mm | 46 | m2 | 0
C | Trenches width > 0.3m
| Maximum depth < 2.00m | 13 | Cu.m | 0
Disposal
D | Excavated material;
Offsite:
| 2km away from the site | 8 | Cu.m | 0
Filling to make up levels
E | Average thickness >0.25m;
arising from the excavations;
Selected laterite in layers exceeding
| 250mm | 5 | Cu.m | 0
F | Average thickness < 0.25m;
Laterite obtained off site
| Selected in layers not exceeding 150mm | 25 | Cu.m | 0
G | Average thickness > 0.25m;
Hardcore obtained off site;
| handpacked | 16 | Cu.m | 0
H | Damp proof membrane laid on blinded surface of hardcore | 46 | Sq.m | 0
E05: IN SITU CONCRETE CONSTRUCTION
GENERALLY
In situ concrete (1:3:6 - 36mm aggregate to
attain minimum works strength of 25N/mm2 in 28
days and poured at a height not more than 3.00m
J | Foundations
Poured on or against earth or unblended
| hardcore | 3 | Cu.m | 0
In situ concrete (1:2:4 - 19mm aggregate) to
attain minimum works strength of 25N/mm2 in 28
days and poured at a height not more than 3.00m
K | Beds
Poured on or against earth or unblended
| hardcore | 7 | Cu.m | 0
| To Collections |  |  | 0
E20: FORMWORK FOR IN SITU CONCRETE
Sawn formwork
A | Sides of foundation
plain vertical
| Height < 250mm | 18 | Lin.m | 0
0
F10: BRICK/BLOCK WALLING
Hollow sandcrete blockwall bedded and jointed
in cement mortar (1:6) and laid in stretcher bond
and filled solid with concrete (1:3:6 - 36mm
aggregate)
B | Walls
230mm thick
| Vertical | 18 | Sq.m | 0
M20: PLASTERED/RENDERED/ROUGHCAST
COATINGS
EXTERNAL
Cement and sand (1:4) smooth rendering
C | Walls
Width >300mm
| 12mm thck | 11 | Sq.m | 0
M60: PAINTING/CLEAR FINISHINGS
Prepare, prime and apply one undercoat and
two finishing coats of 'Berger' or other equal
and approved high quality emulsion paint on
rendered face of wall
D | General Surfaces
| Girth > 300mm | 11 | Sq.m | 0
| To Collections |  |  | 0
COLLECTION
| Page 2 |  |  | 0
| Page 3 |  |  | 0
WORK BELOW THE GROUND FLOOR BED
| carried to summary;- |  |  | 0
EXTERNAL AND INTERNAL WALL
E05: IN SITU CONCRETE CONSTRUCTION
GENERALLY
In situ concrete (1:2:4 - 19mm aggregate) to
attain minimum works strength of 25N/mm2 in 28
days and poured at a height not more than 3.00m
A | Lintels
Isolated
| Reinforced | 1 | Cu.m | 0
E20: FORMWORK FOR IN SITU CONCRETE
Sawn formwork
B | Lintels
Attached to walls
| Rectangular 225 X 225mm | 12 | Sq.m | 0
E30: REINFORCEMENT FOR IN SITU CONCRETE
High tensile reinforcement bars
Bar
C | 10 - 16mm diameter
| Bent | 0.02 | Tones | 0
D | 10mm diameter
| Links | 0.01 | Tones | 0
F10: BRICK/CEMENT BLOCK WALLING
Hollow sandcrete blockwall laid in stretcher bond
bedded and jointed in cement mortar (1:6)
Walls
E | 225mm thick
| vertical | 83 | Sq.m | 0
EXTERNAL AND INTERNAL WALL
| CARRIED TO SUMMARY |  |  | 0
ROOF CONSTRUCTION
AND COVERING
E05: IN SITU CONCRETE CONSTRUCTION
GENERALLY
In situ concrete (1:2:4 - 19mm aggregate) to attain
minimum works strength of 25N/mm2 in 28days
and poured at a height not more than 3.00m
Beams
A | Isolated Reinforced | 1 | Cu.m | 0
E20: FORMWORK FOR IN SITU CONCRETE
Sawn formwork
Beams
B | Attached to walls; Rectangular 225 X 225mm | 12 | Sq.m | 0
E30: REINFORCEMENT FOR IN SITU CONCRETE
High tensile reinforcement bars
Bar
C | 10 - 16mm diameter; Straight | 0.12 | Tones | 0
D | 10mm diameter Links | 0.1 | Tones | 0
G20: CARPENTRY/TIMBER FRAMING/FIRST FIXING
Sawn Hardwood treated with preservatives
Roof Members Pitched
E | 50 X 150mm | 142 | Lin.m | 0
F | 50 X 100mm | 98 | Lin.m | 0
G | 50 X 75mm ditto | 290 | Lin.m | 0
H | 50 X 50mm | 484 | Lin.m | 0
J | 25 X 300mm fascia board | 76 | Lin.m | 0
H31: METAL PROFILED SHEET CLADDING/
COVERING/SIDING
Queen Aluminium' or other equal and approved
0.55mm guage corrugated coloured longspan
aluminium roofing sheet with one and half
corrugation side laps nailed to timber purlins with
and including matching nails (measured nett - no
allowance made for laps)
K | Roof Coverings
| Pitch 200 from horizontal | 280 | Sq.m | 0 |  | 1500000
5357.1429
L | Eaves; 200mm girth | 79 | Lin.m | 0
M | Ridges/hip
| 600mm girth | 62 | Lin.m | 0
ROOF CONSTRUCTION
| carried to summary;- |  |  | 0
WINDOWS
L10: WINDOWS/ROOFLIGHTS/SCREENS/
Chartered Aluminium' or other equal approved
Colour; powder coated extruded standard gauge
aluminium windows, factory glazed with 5mm thick
plain glass; to Architect specification; complete with all
accessories and ironmongery including pinning,
lugging and bedding in cement mortar (1:6) to
concrete or blockwork
Fixed glass, double glazed, double glass windows and frames
A | Size 1200 X 1200mm high | 4 | Nr | 0
B | Size 600 X 600mm high | 4 | Nr | 0
Chartered Aluminium' or other equal approved
Colour; powder coated standard gauge aluminium
casement windows factory glazed with
6mm thick plain glass; with a combined fixed and
sliding insect screen to Architect specification;
complete with all accessories and ironmongery
including pinning and lugging and bedding in cement
mortar (1:6) to concrete or blockwork
Casement windows and window frames
C | Size 1200 X 1200mm high | 4 | Nr | 0
D | Size 600 X 600mm high | 4 | Nr | 0
BURGULAR PROOF
16mm wrot iron bars welded at joint according
to Architect's instruction horizontally at 150mm centres
and vertical at 300mm centres, including pinning, lugging
and bedding in block work or concrete work
E | Size 1200 X 1200mm high | 8 | Nr | 0
F | Size 600 X 600mm high | 8 | Nr | 0
WINDOWS
| carried to summary |  |  | 0
DOORS
DOORS/SHUTTERS/HATCHES
STEEL
Supply and install approved high quality 44mm thick steel Flush doors complete with 50mm thick full jamb frame, sub frame, architrave and Ironmongery including observer view glass bay
Door size
A | 1200 x 2050mm high | 2 | Nr. | 0
B | 900 x 2050mm high | 10 | Nr. | 0
C | 750 x 2050mm high | 3 | Nr. | 0
D | Supply and install approved authomatic door closer | 10 | Nr. | 0
E | Allow for the supply and installation of biometric door
| opener complete with all accessories | 5 | Nr. | 0
| DOORS CARRIED TO SUMMARY |  |  | 0
FITTINGS AND FIXTURES
A | workbenches, wall shelves finished with epoxy/acrylic top finish to Architects design and specifications. Construction of laboratory work bench counter size:7500 (subject to available space) x 750 x 900mm(H) in L shape or other appropriate shape complete with one-piece 20mm thick white polished synthetic marble/Glossy finish Acrylic slab fixed seamless and jointless with appropriate wall cover and splash back, on appropriate 3'' square pipe skeleton, sand blasted and painted against corrosion bolted to floor: with under counter storage cabinet and all exposed surfaces made with white laminate plywood with provision of 1200mm leg spaces and 2 nos embedded double-deep BELFAST ceramic laboratory sink (1no hand wash sink with elbow operated tap and 1 No. Eye wash station) connected to waste system in laboratory counter label clean and dirty area | 1 | Nr | 0
N FURNITURE/EQUIPMENT
| Carried to Summary |  |  | 0
WALL FINISHING
INTERNALLY AND EXTERNALLY
M20: PLASTERED/RENDERED/ROUGHCAST
COATINGS
Cement and sand (1:4) rendering
Walls
A | Width > 300mm
| 13mm thick | 324 | Sq.m | 0
Wall Screeding
B | Prepare and apply POP screeded finish on rendered wall | 336 | Sq.m | 0
-12
Cracks
C | Allow for the general maintenance of cracks on wall | 15 | Sum | 0
M60: PAINTING/CLEAR FINISHINGS
Prepare and apply one undercoat and two finishing
coat of MAYER paint or other equal and approved
high quality satin paint on screeded wall.
General Surfaces
D | Girth > 300mm | 566 | Sq.m | 0
E | Width < 300mm | 228 | Lin.m | 0
EXTERNALLY
M60: PAINTING/CLEAR FINISHINGS
Prepare and apply one undercoat and two finishing
coat of Berger paint or other equal and approved
high quality emulsion paint on rendered wall.
General Surfaces
F | Girth > 300mm | 452 | Sq.m | 0
Knot, prime and apply two finishing coat of Berger
paint or other equal and approved high quality gloss
paint on fascia boards
G | Fascia board | 29 | Lin.m | 0
WALL FINISHING
| CARRIED TO SUMMARY;- |  |  | 0
FLOOR FINISH
M10: CEMENT: SAND/CONCRETE SCREEDS/TOPPINGS
Cement and sand (1:4) screeded bed 40mm thick to
receive floor tilling
A | Floors
| Levels or to falls only < 150 from horizontal | 92 | Sq.m | 0
M40: STONE/CONCRETE/QUARRY/CERAMIC
TILING/MOSAIC
Epoxy Floor Finish
B | Blinding steel surface 50 thick | 92 | Sq.m | 0
General floor surface preparation
C | Surface Preparation; Floor shall be acid washed, so that
all contermination in the floor is completely cleaned and
| ready for to receive epoxy finishes. | 92 | Sq.m | 0
Epoxy Finish
Apply Epoxy Primer Nitoprime 25, manufactured by
applied on a prepared surface and antislip grains spread
over the same to ensure mechanical key with the
subsequent epoxy treatment. Nitoflor TF 5000,
chemical and abrasion resistant epoxy floor screed,
manufactured by Fosroc, shall then be laid by skill
workers @ 3mm thickness on the Primer Nitoprime
25 as per manufacturer's specification.
The screed shall have a conpressive strength of
85N / sqmm and Flexural strength of 28 N / sqmm
Nitroflor TF 5000 is resistant to Acids, Alkalis, Solvents &
Organics and Aqueous solutions. The screed shall
thereafter be sealed with Nitoflor SL2000, chemical &
abrasion resistant epoxy floor topping manufactured by
Fosroc. Nitoflor SL2000 shall be trowel finished to give
a smooth finish with 5mm overall thickness.
D | Epoxy flooring system Internally | 92 | Sq.m | 0
FLOOR FINISHINGS
| CARRIED TO SUMMARY;- |  |  | 0
CEILING FINISHINGS
INTERNAL / EXTERNAL
M20 PLASTERED/RENDERED/ROUGHCAST
COATINGS
M31: FIBROUS PLASTER
In situ cast plaster of paris suspended ceiling slabs
cast to Architect's design including all necessary
accessories and fixing to sofit of concrete floor slab
or hardwood noggings (m/s) Cost to include painting
with appropriate satin of the MEYER type.
A | Ceiling
Width > 300mm
5mm thick
| pannelled slab | 235 | Sq.m | 0
CEILING FINISHINGS
| carried to summary |  |  | 0
SANITARY APPLIANCES/FITTINGS
Fittings, equipment and appliances associated
with services.
A | Supply and install Sensor tap to WHB and Sink
| complete with allaccessories | 7 | Nr | 0
FIRE FIGHTING SYSTEM /DETECTORS
B | Suplly and fix in place DCP ABC - 9Kg Fire Extinguisher | 6 | Nr | 0
SANITARY APPLIANCES/FITTINGS
| CARRIED TO SUMMARY;- |  |  | 0
AIR-CONDITIONING & VENTILATION
Supply, install and commision the fllowing
Air-conditioning equipments (Media or LG)
A | 2.0HP, 18,000btu/Hr Split Air conditioning unit complete | 5 | Nr | 0
B | Allow for A/C steel hanger for AC outdoor units | 5 | Nr | 0
U61: VENTILLATION SYSTEM: HVAC
B | Equipment; 12,500 CuM/hr single phase, 8kw ducted extractor units with H12 and H14 HEPA filters with all accessories and manual/programable controls. Cost to include ducting and controls | 2 | Units | 0
C | Inverter air conditioner with 9000 Btu capacity with
| both thermostattic and remote control Units | 5 | nr | 0
D | 8,000 m3/h AHU with HEPA filtration system, and cooling units of the type York or equivalent with 4 pipe, 4 way cassette 1328m3/h with fresh air supply system with both thermostattic and remote control Units for manual and programable settings. Cost to include ducting and all assessories. | 2 | Units | 0
Builders work in connection with Air-conditioning & Ventilation
E | Allow for the installation of HVAC system, testing and commissioning to Engineers design and specification |  | Sum | 0
| HVAC to Summary |  |  | 0
ELECTRICAL INSTALLATIONS
Y73: LUMINAIRES AND LAMPS
Philips or other equal and approved, complete
with conduit boxes patteraes, ceiling roses,
connector blocks, flexible cords, starters, chokes
capacitors, shades, diffusers, reflectors etc
Luminaires
A | Ceiling mounted fittings complete with energy saving
bulb plugged and screwed to concrete soffits.
| Drop < 1.00m | 50 | Nr | 0
B | 1 x 100W Bulk head wall mounted security
lighting fittings plugged and screwed to wall
| Drop < 1.00m | 12 | Nr. | 0
| ELECTRICAL INSTALLATION |  |  | 0
V33: SOLAR POWER INSTALLATION
A | 6V 600 AH Batteries | 16 | Nr | 0
B | 320 Watt solar panels | 64 | Nr | 0
C | 20 KVA 48V Inverter | 2 | Nr | 0
D | 200A MPPT charge controller | 2 | Nr | 0
E | Twisted solar cables | 3 | Nr | 0
F | Hanger for Batteries | 1 | item | 0
G | Hanger for Panels(free standing) | 1 | item | 0
H | Programming and installation charge |  | item | 0
| SOLAR POWER INSTALLATION CARRIED TO SUMMARY |  |  | 0
SUMMARY
| DEMOLITION WORK |  |  | 0
| SUBTRUCTURE |  |  | 0
| INTERNAL AND EXTERNAL WALLS |  |  | 0
| ROOF |  |  | 0
| WINDOWS |  |  | 0
| DOORS |  |  | 0
| FITTINGS AND FIXTURES |  |  | 0
| WALL FINISHINGS |  |  | 0
| FLOOR FINISHINGS |  |  | 0
| CEILING FINISHINGS |  |  | 0
| SANITARY APPLIANCES/FITTINGS |  |  | 0
| AIR-CONDITIONING & VENTILATION |  |  | 0
| ELECTRICAL INSTALLATION |  |  | 0
| SOLAR POWER INSTALLATION |  |  | 0
| SUB TOTAL CARRIED TO GENERAL SUMMARY |  |  | 0

## SUMMARY
BILL OF QUANTITIES FOR THE PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LABS AT DR. LAWRENCE HENSHAW MEMORIAL HOSPITAL CALABAR, CROSS-RIVER STATE
GENERAL SUMMARY
S/No. | Name | No. of Units | Amount (NGN) | Total Amount (NGN)
1 | Preliminaries and General Works | 1 | 0 | 0
2 | BOQ Calabar Laboratory Upgrade | 1 | 0 | 0
Total |  |  |  | 0
TOTAL COST OF REXPANSION/MODIFICATION WORKS |  |  |  | 0