## COVER
NATIONAL AGENCY FOR THE CONTROL OF AIDS (NACA) WITH FUNDING FROM GLOBAL FUND
RENOVATION AND UPGRADE OF SELECTED PUBLIC HEALTH LABORATORIES IN THE SIX GEOPOLITICAL ZONES IN NIGERIA AND THE NATIONAL EXTERNAL QUALITY ASSESSMENT LABORATORY (NEQAL) UNDER THE GLOBAL FUND RESILIENT & SUSTAINABLE SYSTEMS FOR HEALTH [RSSH] II PROJECT GRANT
LOT 5
PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LABORATORY AT NASIDARC, NASSARAWA STATE
BILL OF QUANTITIES
DECEMBER, 2021

## PRELIMINARIES
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT (N:K)
BILL No 1: PRELIMINARIES
A | Drawings
B | Setting Out
C | Site accomodation for contractor/Storage
D | Water for works
E | Watching and Lighting
F | Security for the works
G | Welfare and Safety
H | First Aid Box
J | Scaffolding
K | Progress Photographs
L | Records
M | Foreman on Site
N | Sign and notice Board
O | Protection for the Works
P | Plant, tools and equipment
Q | Site accomodation for employer representative
R | Clearing / Cleaning
BILL NO 1: PRELIMINARIES CARRIED TO
| GENERAL SUMMARY-: |  |  |  | 0

## LABORATORY NASSARAWA
BILL OF QUANTITIES FOR THE PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LABS AT NASIDARC, NASSARAWA STATE
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
ELEMENT Nr. 1
DEMOLITION AND ALTERATION
ROOF
H72: Aluminium sheet coverings/flashings
A | Allow a provisonal sum of N500,000 for mending of roof leakage |  | Sum |  | 0
B | Allow a provisional sum of 200,000.00 for removing tile ceiling |  | Sum |  | 0
| DEMOLITION AND ALTERATION CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 2
INTERNAL AND EXTERNAL WALLS
Aluminum powder coated factory glazed partition walls; door frames sealed airtight, built into blockwork and concrete surround, bedded and pointed in cement and sand mortar with mastic sealant complete with all necessary Ironmongery with door closer mechanism
A | Partition fixed glass Wall (10mm thick glazing) | 159 | m2 |  | 0
| INTERNAL AND EXTERNAL WALLS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 3
WINDOWS
| L11: Metal windows/rooflights/sceens/louvres |  |  |  | 0
| Aluminium Casement windows or approved equal in 6mm thick tintedglass framed in powder coated approved coloured aluminium profilesincluding 15mm thick steel sub frame and Aluminium Lever handles tomatch window frames, complying to Architect's details, built intoblockwork and pointed in cement sand mortar |  |  |  | 0
0
A | window size 1200 x 1200mm high | 4 | Nr |  | 0 | 34722.2222
B | window size 600 x 600mm high | 2 | Nr |  | 0
0
| Buglary Proof Bars |  |  |  | 0
Steel burglary proffing bars to Architects detailed drawings
0
C | Window size 1200 x 1200mm high | 4 | Nr |  | 0
0
D | Window size 600 x 900mm high | 2 | Nr |  | 0
| WINDOWS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 4
DOORS
L21: Metal doors/shutters/hatches
Aluminum powder coated factory glazed doors with aluminium Lever handles to match door frames sealed airtight, built into blockwork and concrete surround, bedded and pointed in cement and sand mortar with mastic sealant complete with all necessary Ironmongery with door closer mechanism
A | Door, double leaf inward opening, size 1200 x 2100mm high | 6 | nr |  | 0
Steel panel security doors built into built blockwork and
concrete surround, bedded and pointed in cement and sand
mortar with mastic sealant complete with all necessary Iron
mongery
0
B | Steel panel with glass door size 900 x 2100mm high | 10 | nr |  | 0
0
C | Security door size 900x2100mm high | 1 | nr |  | 0
| DOORS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 5
FIXTURES AND FITTINGS
N10: General fixtures/furnishings/equipment
STORE SHELVES
A | Allow a Provisional Sum of N500,000.00 for store shelves to
| Architects design and specifications |  | sum |  | 0
| FIXTURES AND FITTINGS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 6
WALL FINISHES
M20: Plastered/Rendered/Roughcast coatings
15mm thick cement and sand (1:3) floated smooth synthetic renderingto general surfaces complying to Architect's details.
A | Internal walls srceeding to receive paint | 860 | m2 |  | 0
0
M60: Painting/Clear finishing
Emulsion paint as manufactured by Berger or Dulux in 3 coats to
floated surfaces, rate including floating to Architect's details.
B | Apply walls with Stuco paint internally | 860 | m2 |  | 0
0
C | Apply wall with dulux paint Externally | 309.3 | m2 |  | 0
0
| WALL FINISHES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 7
CEILING FINISHES
K40: Suspended Ceiling
P.O.P ceiling lining fixed to 50x50mm timber noggins
and soffit of suspended slab
A | POP Ceiling finish | 287 | m2 |  | 0
| CEILING FINISHES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 8
FLOOR FINISHES
M10: Sand cement/Concrete/Granolithic
screeds/flooring
General floor surface preparation
A | Surface Preparation; Floor shall be acid washed, so that all
contermination in the floor is completely cleaned and ready
| for to receive epoxy finishes. | 274 | Sq.m |  | 0
Epoxy Finish
Apply Epoxy Primer Nitoprime 25, manufactured by Fosroc,
applied on a prepared surface and antislip grains spread over
the same to ensure mechanical key with the subsequent
epoxy treatment. Nitoflor TF 5000, chemical and abrasion
resistant epoxy floor screed, manufactured by Fosroc,
shall then be laid by skill workers @ 3mm thickness on the
Primer Nitoprime 25 as per manufacturer's specification.
The screed shall have a conpressive strength of
85N / sqmm and Flexural strength of 28 N / sqmm Nitroflor
TF 5000 is resistant to Acids, Alkalis, Solvents & Organics and
Aqueous solutions. The screed shall thereafter be
sealed with Nitoflor SL2000, chemical & abrasion resistant
epoxy floor topping manufactured by Fosroc. Nitoflor SL2000
shall be trowel finished to give a smooth finish with 5mm overall
thickness.
B | Epoxy flooring system Internally | 274 | Sq.m |  | 0
| FLOOR FINISHES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 9
ELECTRICAL SERVICES
V20: LV Distribution
Equipment; Metal clad Main Distrbution Board surface/ flush
type as manufacured by ABB or approved equal including all
MCB, back outlet connections to flush adaptable boxes, earth
bonding, labels and fixing in accordance with manufacturer's
instructions
A | 100A 8-Way TP&N MCB Distribution Board complete with
100A integral incoming isolator and comprising 3nr 10A
stablock; 4nr 5A stablock; 5nr 30A stablock and 11nr 20A
| stablock | 1 | nr |  | 0
Equipment; Metal clad ELCB Board surface/ flush type as
manufacured by ABB or approved equal including all MCB,
back outlet connections to flush adaptable boxes, earth
bonding, labels and fixing in accordance with manufacturer's
instructions
B | 63A TP&N ELCB | 1 | No |  | 0
C | Meter - cut -out fuses | 4 | No |  | 0
V21: General lighting
LED lighting, ceiling recessed and mounyed with sealed edges
Mounted on POP finished ceiling. Cost to include making good
disturbed surfaces.
D | LED lighting ceiling
| 45w | 20 | nr |  | 0
0
E | 15w | 50 | nr |  | 0
0
A | 8x60w satin blow glass baloon lighting fitting |  | nr
B | 1x75w pendant fitting in satin glass and frosted ceiling cup
| lighting fitting | 20 | nr
C | Ceiling mount fitting in die cast Aluminium reflector lamp type:
| 1x60w incandescent lighting fitting | 20 | nr
D | Pressed metal white varnish ceiling fitting lamp, 1 x 60w |  | nr
E | 1500mm sweep decorative ceiling fan complete with regulator
| 5-Speed regulator | 4 | nr
V22: General LV Power
Final Circuit; PVC insulated and colour coded copper cable
drawn into 20 diamter concealed UPVC conduit; rates to
include for all cables and conduits for switches, sockets and
other accessories for complete installation
Cables and Conduits in final circuits
F | 13A 1 Gang double pole white moulded socket outlet flush to
| BS 1363: PART:2:1995 MK or approved equal |  | nr
G | 13A 2 Gang double pole white moulded socket outlet flush to
| BS 1363: PART:2:1995 MK or approved equal |  | nr
H | 20A 3 Pin 1 Gang switched socket outlet flush to BS S46:7950 |  | nr
MK or approved equal
F | 15A 3 Pin 1 Gang double pole white moulded socket outlet
| flush to BS 1363: PART:2:1995 MK or approved equal | 5 | nr |  | 0
Y60: Conduit and cable trunking
Conduit; strength PVC pipe with flange joints in chases/floor screeds
with and inlcuding conduit boxes, locknuts, brushes, couplers, bends,
reducers, cutting and other necessary accessories, rates including
making good surfaces disturbed.
G | 20mm Diameter | 110 | m |  | 0
Y61: HV/LV cable and wiring
Cables; PVC insulated cable as manufactured by NOCACO or
approved equal drawn into conduits or ducts or laid down into trunking
or laid in trenches including cable loops, terminations, glands and all
other accessories
H | 2 x 1c 2.5mm2 PVC copper cable | 225 | m |  | 0
| ELECTRICAL SERVICES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 10
V33: SOLAR POWER INSTALLATION
A | 6V 600 AH Batteries | 16 | Nr |  | 0
B | 320 Watt solar panels | 32 | Nr |  | 0
C | 20 KVA 48V Inverter or equal and approved | 1 | Nr |  | 0
D | 200A MPPT charge controller | 2 | Nr |  | 0
E | Twisted solar cables | 3 | Nr |  | 0
F | Hanger for Batteries | 1 | item |  | 0
G | Hanger for Panels(free standing) | 1 | item |  | 0
H | Programming and installation charge |  |  | 0 | 0
| SOLAR POWER INSTALLATION CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr 11
PLUMBING AND MECHANICAL SERVICES
Y10: Pipelines
COLD WATER SUPPLY PIPES, GALVANISED iron pipe
to BS 425
A | Allow for complete replacement of existing but damaged
supply/waste piping with appropriate UPVC pressure pipe
to be executed complete, including making good all other
| faults as may be directed |  | Sum |  | 0
Y25: General pipeline equipment
Equipment; supply, install and connect up
pipeline equipment as manufactured by
ARMITAGE SHANKS or approved equal with all
necessary accessories for complete installation
B | Washhand basin (510 x 410mm) complete with pedestral
centre tap, 13mm diameter chrome plated pillar tap, plastic
bottle trap, 80mm slotted chrome plated union waste,
Aluminium brackets and other relevant accessories, pedestal
| crewed to the wall | 7 | nr |  | 0
R12: Drainage above ground
SOIL PIPES, UPVC pipes to BS 4660 or DIN 8062,10 bar
C | 50mm Diameter | 43 | m |  | 0
EDS system of the type DHIS or equivalent. Cost to include installtion
D | 200 liter | 1 | nr |  | 0
FIRE FIGHTING SYSTEMS
Supply, deliver to site and install the following items complete
with all necessary installation and operational accessories
E | Fe-ABC, 9Kg Class K, Amerex Model 2160 for kitchen installation | 5 | nr |  | 0
Fitting and Accessories
F | Allow a provisional Sum of N50,000.00 for other necessary
| items for complete installation of the drainage system |  | Sum |  | 0
Testing and Connection
G | Allow a Provisional Sum of N50,000.00 for testing entire
| pipe network |  | Sum |  | 0
U61: VENTILLATION SYSTEM:
H | Equipment; Supply and Installation of Xplepair or approved equal Unidirectional Flow Ducted Unit Extractor Fan complete with sealant and necessary installation accessories. | 4 | Units |  | 0
| PLUMBING AND MECHANICAL SERVICES CARRIED TO SUMMARY |  |  |  | 0
MAIN SUMMARY
1 | DEMOLITION AND ALTERATION |  |  |  | 0
2 | INTERNAL AND EXTERNAL WALLS |  |  |  | 0
3 | WINDOWS |  |  |  | 0
4 | DOORS |  |  |  | 0
5 | FITTING AND FIXTURES |  |  |  | 0
6 | WALL FINISHES |  |  |  | 0
7 | CEILING FINISHES |  |  |  | 0
8 | FLOOR FINISHES |  |  |  | 0
9 | ELECTRICAL SERVICES |  |  |  | 0
10 | SOLAR POWER INSTALLATION |  |  |  | 0
11 | PLUMBING AND MECHANICAL SERVICES |  |  |  | 0
| TOTAL CARRIED TO GENERAL SUMMARY |  |  |  | 0

## SUMMARY
BILL OF QUANTITIES FOR THE PROPOSED EXPANSION/MODIFICATION OF EXISTING PCR LAB AT NASIDARC, NASSARAWA STATE
GENERAL SUMMARY
S/No. | Name | No. of Units | Amount (NGN) | Total Amount (NGN)
1 | Bill Nr. 1 Preliminaries and General Works | 1 | 0 | 0
2 | Bill Nr 2 Main Facility | 1 | 0 | 0
TOTAL COST OF REXPANSION/MODIFICATION WORKS |  |  |  | 0