## COVER
NATIONAL AGENCY FOR THE CONTROL OF AIDS (NACA) WITH FUNDING FROM GLOBAL FUND
RENOVATION AND UPGRADE OF SELECTED PUBLIC HEALTH LABORATORIES IN THE SIX GEOPOLITICAL ZONES IN NIGERIA AND THE NATIONAL EXTERNAL QUALITY ASSESSMENT LABORATORY (NEQAL) UNDER THE GLOBAL FUND RESILIENT & SUSTAINABLE SYSTEMS FOR HEALTH [RSSH] II PROJECT GRANT
LOT 7
PROPOSED EXPANSION/MODIFICATION OF EXISTING PUBLIC HEALTH LABORATORY, AKURE, ONDO STATE
BILL OF QUANTITIES
DECEMBER, 2021

## PRELIMINARIES
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT (N:K)
BILL No 1: PRELIMINARIES
A | Drawings
B | Setting Out
C | Site accomodation for contractor/Storage
D | Water for works
E | Watching and Lighting
F | Security for the works
G | Welfare and Safety
H | First Aid Box
J | Scaffolding
K | Progress Photographs
L | Records
M | Foreman on Site
N | Sign and notice Board
O | Protection for the Works
P | Plant, tools and equipment
Q | Site accomodation for employer representative
R | Clearing / Cleaning
S | Contract Administration
BILL NO 1: PRELIMINARIES CARRIED TO
| GENERAL SUMMARY-: |  |  |  | 0

## LABORATORY
BILL OF QUANTITIES FOR THE PROPOSED EXPANSION/MODIFICATION OF EXISTING PUBLIC HEALTH LABORATORY, AKURE ONDO STATE
S/N | DESCRIPTION | QTY | UNIT | UNIT RATE | AMOUNT
ELEMENT Nr. 1
SUBSTRUCTURE
D20: Excavation and Filling.
A | Allow for demolition and alteration works and carting away of |  | sum |  | 0
debris.
B | Site preparation; clearing vegetation, bushes and remove
topsoil maximum depth not exceeding 150mm, dispose in
| spoil heap away from site | 139 | m2 |  | 0
0
C | Excavating trenches, width exceeding 0.3m maximum depth |  |  |  | 0
| not exceeding 2.00m | 45 | m3 |  | 0
D | Excavating pits, maximum depth not exceeding 3.00m | 4 | m3 |  | 0
0
E | Disposal excavated materials off site, in spoil heap away from |  |  |  | 0
| site | 15 | m3 |  | 0
0
F | Allow for keeping the surface of the site and the excavation |  |  |  | 0
| free of surface water | 1 | item |  | 0
0
G | Level and compact bottom of excavation to receive concrete in |  |  |  | 0
| foundation | 97 | m2 |  | 0
0
H | Anti-termite treatment surfaces of excavations | 97 | m2 |  | 0
0
J | Filling to excavations around foundations average thickness
| exceeding 250mm, with selected excavated materials |  |  |  | 0
| arising from excavations | 12 | m3 |  | 0
0
K | Filling to make up levels, average thickness exceeding |  |  |  | 0
| 250mm with natural occuring laterite materials obtained off |  |  |  | 0
| site | 11 | m3 |  | 0
E10: In situ concrete
| Plain; Concrete Grade 15; developing minimum 20N/mm2 work straight in 28days |  |  |  | 0
L | Blinding beds under foundation and pits thickness not |  |  |  | 0
| exceeding 150mm | 12 | m3 |  | 0
0
| Plain; Concrete Grade 20; developing minimum 20N/mm2 work straight in 28days |  |  |  | 0
M | Foundations | 28 | m3 |  | 0
0
| Carried to collection |  |  |  | 0
E30: Reinforcement for in situ concrete
Reinforced; Concrete Grade 25; developing minimum 20N/mm2 work straight in 28days
A | Beds and ramps; thickness not exceeding 150-300mm,
| slope not exceeding 150 | 3 | m3 |  | 0
0
B | Column bases/columns | 2 | m3 |  | 0
E20: Formwork for in situ concrete
Plain vertical sawn wrought formwork
C | Edges of beds, height not exceeding 250mm | 15 | m |  | 0
0
D | Columns | 27 | m2 |  | 0
0
E30: Reinforcement for in situ concrete(Provisional)
| High tensile bars to BS 4449, straight |  |  |  | 0
E | 10 - 25mm Diameter | 0.38 | Ton |  | 0
0
| High tensile bars to BS 4449, bent |  |  |  | 0
F | 10 - 25mm Diameter | 0.15 | Ton |  | 0
0
| Fabric mesh A142 weighting 300kg/m2 laid as detailed in |  |  |  | 0
| manufacturer's manual |  |  |  | 0
0
G | Ground floor bed/Attached step | 21 | m2 |  | 0
F10: Brick/Block walling
Sandcrete hollow blockwork in stretcher bond, bedded in
cement and sand mortar mix (1:6), flush pointed and filled
solid with lean concrete,
H | Walls, 255mm thick vertical | 67 | m2 |  | 0
J20: Mastic asphalt tanking/damp proof membranes
J | Flooring and underlay; 0.15mm thick polythene
damp proof membrane width exceeding 300mm
| laid on hardcore blinding | 20 | m2 |  | 0
| Carried to collection |  |  |  | 0
0
Collection
| Page | 2 |  |  | 0
| Page | 3 |  |  | 0
| SUBSTRUCTURE CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 2
FRAMES
E10: In situ concrete
Reinforced; Concrete Grade 25; developing minimum 20N/mm2 work straight in 28days
A | Columns | 3 | m3 |  | 0
0
B | Roof; Beams | 2 | m3 |  | 0
E20: Formwork for in situ concrete
Plain vertical sawn wrought formwork
1000
C | Sides of Columns | 180 | m2 |  | 0
[5 empty] | 0 |  | 1
D | Sides and Soffit of Beams | 50 | m2 |  | 0
| E30: Reinforcement for in situ concrete(Provisional) | [5 empty] | 0.5
High tensile bars to BS 4449, straight
E | 10 - 25mm Diameter | 0.6 | ton |  | 0
High tensile bars to BS 4449, bent
F | 10 - 25mm Diameter | 0.5 | ton |  | 0
G | Supply and fix in place steel poles for walkway complete
| with all associated works. | 40 | Nr |  | 0
| FRAMES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 3
ROOF
G20: Carpentary/Timber framing/First fixing
Sawn, seasoned and solgnum-treated agbura, opepe, ikhimi
or equal approved hardwood in pitched roof members
A | Tie beams 50 x 150mm | 120 | m |  | 0
0
B | Struts 50 x 150mm | 180 | m |  | 0
0
C | Rafters 50 x 150mm | 250 | m |  | 0
0
D | Purlins 50 x 75mm | 300 | m |  | 0
0
E | Noggins 50 x 50mm | 75 | m |  | 0
0
F | Fascia board 300 x 25mm | 170 | m |  | 0
H72: Aluminium sheet coverings/flashings
0.55mm long span terracota red Aluminium coverings fixed to
timber purlins in accordance to manufacturer's details
G | Pitched covering | 360 | m2 |  | 0
0
H | Ridge cappings, girth 600mm | 150 | m |  | 0
0
J | Hip cappings, girth 600mm | 98 | m |  | 0
0
K | Gutter valley, girth 600mm | 36 | m |  | 0
L | Eave cappings, girth 600mm | 64 | m |  | 0
Gloss paint as manufactured by Berger or Dulux in 3 coats to
floated surfaces, to Architect's details.
M | Surfaces of fascia board, width not exceeding 300mm | 169 | m |  | 0
0
| ROOF CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 4
INTERNAL AND EXTERNAL WALLS
F10: Brick/Block/Glass walling
Sandcrete blockwork in stretcher bond bedded in cement and
sand mortar mix (1:4) flush pointed with developing strength
of 5N/mm2
A | Walls, 255mm thick vertical | 215 | m2 |  | 0
0
B | Fabricate and install aluminium partition walling comprising;-
8mm Double glazed tainted glassfixed in place to aluminium
frames complete with other associated works and accessories
| walls flush and sealed joint with POP CEILING as may be | 58 | m2 |  | 0
directed by the project supervisor in;Size : 3.0m x 19.33m
| INTERNAL AND EXTERNAL WALLS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 5
| E10: In situ concrete |  |  |  | 0
| Reinforced; Concrete Grade 25; developing minimum 20N/mm2 work straight in 28days |  |  |  | 0
0
A | Lintels |  |  |  | 0
0
| E20: Formwork for in situ concrete | 1 | m3 |  | 0
Plain vertical sawn wrought formwork
B | Sides and soffits of Lintels | 55 | m2 |  | 0
| E30: Reinforcement for in situ concrete(Provisional) | 45 | m2 |  | 0
High tensile bars to BS 4449, straight
C | 10 - 25mm Diameter | 0.07 | ton |  | 0
High tensile bars to BS 4449, bent
D | 10 - 25mm Diameter | 0.04 | ton |  | 0
WINDOWS
L11: Metal windows/rooflights/sceens/louvres
Procure and install Aluminium Fixed windows or approved equal in
5mm thick tinted double layer glass framed in powder coated
approved coloured aluminium profiles including 15mm thick steel
( double coated with anti-rust) sub frame with burglar proof and
Aluminium Lever handles to match window frames, complying to
Architect's details. Make good all disturbed surfaces.
E | Window size 1200 x 1800mm high | 2 | Nr |  | 0
0
F | Window size 600 x 1200mm high | 4 | Nr |  | 0
0
G | Window size 900 x 900mm high | 2 | Nr |  | 0
H | Window size 1500 x 1200mm high | 1 | Nr |  | 0
0
J | Window size 2700 x 1200mm high | 5 | Nr |  | 0
External Steel burglary proffing bars to Architects detailed drawings
0
K | Window size 1200 x 1800mm high | 2 | Nr |  | 0
L | Window size 600 x 1200mm high | 4 | Nr |  | 0
M | Window size 900 x 900mm high | 2 | Nr |  | 0
N | Window size 1500 x 1200mm high | 1 | Nr |  | 0
P | Window size 2700 x 1200mm high | 5 | Nr |  | 0
| WINDOWS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 6
DOORS
L11: Metal windows/rooflights/sceens/louvres
Aluminum powder coated factory glazed doors with aluminium
Lever handles to match door frames sealed airtight, built into
blockwork and concrete surround, bedded and pointed in
cement and sand mortar with mastic sealant complete with
all necessary Ironmongery with door closer mechanism
A | Double leaf double swing Aluminium Swing Doors approved
powder coated aluminum framed fire resistant, 8mm glass and
aluminum frame with and including 15mm steel subframe
| etc. Overall size 1500 x 2100mm high | 1 | Nr |  | 0
0
L20: Timber doors/shutters/hatches
40mm thick timber rebated polished HDF non-absorbent
Flush door, with 50 x 12mm hardwood timber sub-frame
including ironmongery, kick plates, push plates and overhead
door closer; and 3no Hinges for rebated door; and architraves
complying to Architect's details. All door finish should be
scratch-proof, non-absorbent and rubber gasket sealed.
Complete with all assesories
B | Door, 900 x 2100mm high | 18 | nr |  | 0
C | Door, 750 x 2100mm high | 4 | nr |  | 0
Door stops
D | Floor mounted door stop | 22 | Nr |  | 0
Mortice locks
E | Union J9205 AB. Double cylinder Knobset with 3 keys in
| Anodized Bronze finish (utilities) GMK with decorative rose | 22 | Nr |  | 0
0
| DOORS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 7
FIXTURES AND FITTINGS
N10: General fixtures/furnishings/equipment
LABORATORY CABINETS
A | Allow a Provisional Sum of N4,500,000.00 for Acrylic laboratory |  | sum |  | 0
workbenches, wall shelves finished with epoxy/acrylic top finish
to Architects design and specifications.Construction of laboratory work bench counter size:7500 (subject to available space)x750x900mm(H) in L shape or other appropriate shape complete with one-piece 20mm thick white polished synthetic marble/Glossy finish Acrylic slab fixed seamless and jointless with appropriate wall cove and splash back, on appropriate 3'' square pipe skeleton, sand blasted and painted against corrosion bolted to floor: with under counter storage cabinet and all exposed surfaces made with white laminate plywood with provision of 1200mm leg spaces and 2 nos embedded double-deep BELFAST ceramic laboratory sink (1no hand wash sink with elbow operated tap and 1 No. Eye wash station) connected to waste system in laboratory counter label clean and dirty area
STORE SHELVES
B | Allow a Provisional Sum of N650,000.00 for store shelves to |  | sum |  | 0
Architects design and specifications
C | Supply standard adjustable height laboratory stools with backrest covered with non-absorbent non-synthetic material | 10 | nr |  | 0
| FIXTURES AND FITTINGS CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 8
WALL FINISHES
M20: Plastered/Rendered/Roughcast coatings
15mm thick cement and sand (1:3) floated smooth synthetic rendering
to general surfaces complying to Architect's details.
A | Walls, Internally width exceeding 300mm | 255 | m2 |  | 0
B | Walls externally, width exceeding 300mm | 230 | m2 |  | 0
M40: Stone/ConcreteQuarry/Ceramic tilling/Mosaic
200 x 300 x 6mm thick coloured glazed ceramic wall tilling
C | laid on cement and sand backing | 35 | m2 |  | 0
D | Walls, width exceeding 300mm | 15 | m |  | 0
M60: Painting/Clear finishing
Emulsion paint (satin finish) as manufactured by Berger or
Dulux in 3 coats to floated surfaces, rate including floating
to Architect's details.
E | Walls, Internally width exceeding 300mm | 714 | m2 |  | 0
| WALL FINISHES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 9
CEILING FINISHES
K40: Suspended Ceiling
P.O.P ceiling lining fixed to 50x50mm timber noggins
and soffit of suspended slab. Cost to include final paint finish.
A | Ceiling lining | 456 | m2 |  | 0
B | Ditto, Cornices | 127 | m |  | 0
M60: Painting/Clear finishing
Emulsion paint (satin finish)as manufactured by Berger/
Dulux in 3 coats to floated surfaces, rate including floating
to Architect's details.
C | Surfaces, width exceeding 300mm | 456 | m2 |  | 0
D | Surfaces, width not exceeding 300mm | 127 | m |  | 0
| CEILING FINISHES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 10
FLOOR FINISHES
M10: Sand cement/Concrete/Granolithic
screeds/flooring
25mm thick cement and sand (1:4) floated bed to general
surfaces to receive further finishes
A | Floors, level and to falls only not exceeding 150 from
| horinzontal | 150 | m2 |  | 0
M40: STONE/CONCRETE/QUARRY/CERAMIC
TILING/MOSAIC
OFFICE TILING
600 x 600 x 10mm thick glazed vitrified floor tiles laid on
cement and sand (1:4) screeded bed and pointed all
round the edges with cement
B | Floors; Levels or to falls only < 150 from horizontal | 22 | Sq.m |  | 0
C | Skirting; 100mm high | 37 | Lin. M |  | 0
M40: Stone/ConcreteQuarry/Ceramic tilling/Mosaic
epoxy floor finish , no less than 3mm thick, of the type Sazota
or equivalent laid on roughened tile surface including wall
coves to Architect's details
D | Floors; level and to falls only not exceeding 150 from
| horinzontal | 150 | m2 |  | 0
| FLOOR FINISHES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 11
ELECTRICAL SERVICES
V20: LV Distribution
Equipment; Metal clad Main Distrbution Board surface/ flush
type as manufacured by ABB or approved equal including all
MCB, back outlet connections to flush adaptable boxes, earth
bonding, labels and fixing in accordance with manufacturer's
instructions
A | 100A 8-Way TP&N MCB Distribution Board complete with
100A integral incoming isolator and comprising 3nr 10A
stablock; 4nr 5A stablock; 5nr 30A stablock and 11nr 20A
| stablock | 1 | nr |  | 0
Equipment; Metal clad ELCB Board surface/ flush type as
manufacured by ABB or approved equal including all MCB,
back outlet connections to flush adaptable boxes, earth
bonding, labels and fixing in accordance with manufacturer's
instructions
B | 63A TP&N ELCB | 3 | No |  | 0
C | Meter - cut -out fuses | 4 | No |  | 0
V21: General lighting
Lamp and luminaires; lighting fittings as manufactured by
TECHNOLUX or approved equal fixed to soffit of POP including all
necessary for complete installation
D | Incandescent vandal resistant bulkhead light fitting lamp type
| 1x 15w white LED lighting fitting | 30 | nr |  | 0
E | Ceiling mount fitting and flush to surface: | 10 | nr |  | 0
1x10w LED lighting fitting
F | Pressed metal white varnish ceiling fitting lamp, 1 x 10w | 6 | nr |  | 0
V22: General LV Power
Final Circuit; PVC insulated and colour coded copper cable
drawn into 20 diamter concealed UPVC conduit; rates to
include for all cables and conduits for switches, sockets and
other accessories for complete installation
Cables and Conduits in final circuits
G | 13A 1 Gang double pole white moulded socket outlet flush to
| BS 1363: PART:2:1995 MK or approved equal | 10 | nr |  | 0
H | 13A 2 Gang double pole white moulded socket outlet flush to
| BS 1363: PART:2:1995 MK or approved equal | 7 | nr |  | 0
| Carried to collection |  |  |  | 0
A | 20A 3 Pin 1 Gang switched socket outlet flush to BS S46:7950 | 8 | nr |  | 0
MK or approved equal
B | 15A 3 Pin 1 Gang double pole white moulded socket outlet
| flush to BS 1363: PART:2:1995 MK or approved equal | 14 | nr |  | 0
C | 45A Double pole cooker unit with neon indicators flush to BS
| 4177:1992 MK or approved equal | 5 | nr |  | 0
D | RJ11 Telephone oultlet MK or approved equal | 3 | nr |  | 0
Y60: Conduit and cable trunking
Conduit; strength PVC pipe with flange joints in chases/floor screeds
with and inlcuding conduit boxes, locknuts, brushes, couplers, bends,
reducers, cutting and other necessary accessories, rates including
making good surfaces disturbed.
E | 20mm Diameter | 125 | m |  | 0
F | 25mm Diameter | 20 | m |  | 0
Y61: HV/LV cable and wiring
Cables; PVC insulated cable as manufactured by NOCACO or
approved equal drawn into conduits or ducts or laid down into trunking
or laid in trenches including cable loops, terminations, glands and all
other accessories
G | 2 x 1c 2.5mm2 PVC copper cable | 483 | m |  | 0
H | 2 x 1c 4mm2 PVC copper cable | 188 | m |  | 0
J | 10mm2 PVC/SWA/PVC copper cable | 90 | m |  | 0
K | 4c 16mm2 PVC/SWA/PVC copper cable | 35 | m |  | 0
Y74: Accessories for Electrical services
Final Circuit; PVC insulated and colour coded copper cable
drawn into 20 diamter concealed UPVC conduit; rates to
include for all cables and conduits for lighting points, switches
and other accessories for complete installation
Cables and Conduits in final circuits
L | 10a 1 gang 1 way switch white moulded range | 10 | nr |  | 0
M | 10a 2 gang 1 way switch white moulded range | 15 | nr |  | 0
N | 10a 1 way intermediate switch white moulded range | 10 | nr |  | 0
| Carried to collection |  |  |  | 0
V32: Earthing and Lighting Protection
Ancillary; Supply and installation earthing and
lighting protection system
A | Alow for complete earthing of Building and bonding of all metal parts |  | Sum |  | 0
B | Allow a provisional sum of N300,000.00 for any outstanding
| works that may not have been captured under Electrical services. |  | Sum |  | 0
| Carried to collection |  |  |  | 0
Collection
| Page | 12 |  |  | 0
| Page | 13 |  |  | 0
| Page | 14 |  |  | 0
| ELECTRICAL SERVICES CARRIED TO SUMMARY |  |  |  | 0
ELEMENT Nr. 12
V33: SOLAR POWER INSTALLATION
A | 6V 600 AH Batteries | 16 | Nr |  | 0
B | 320 Watt solar panels | 32 | Nr |  | 0
C | 20 KVA 48V Inverter | 1 | Nr |  | 0
D | 200A MPPT charge controller | 2 | Nr |  | 0
E | Twisted solar cables | 3 | Nr |  | 0
F | Hanger for Batteries | 1 | item |  | 0
G | Hanger for Panels(free standing) | 1 | item |  | 0
H | Programming and installation charge |  | sum |  | 0
SOLAR POWER INSTALLATION
| CARRIED TO SUMMARY;- |  |  |  | 0
ELEMENT Nr. 13
PLUMBING AND MECHANICAL SERVICES
Y10: Pipelines
A | Allow the sum of N250,000.00 for all plumbing installations |  | sum |  | 0
Y25: General pipeline equipment
Equipment; supply, install and connect up
pipeline equipment as manufactured by
ARMITAGE SHANKS or approved equal with all
necessary accessories for complete installation
B | Water closet "P" or "S" trap close couple washdown unit in
white vitreous China complete with 9 litres capacity cistern,
| volume of regulator and other necessary accessories | 4 | nr |  | 0
C | Washhand basin (510 x 410mm) complete with pedestral
centre tap, 13mm diameter chrome plated pillar tap, plastic
bottle trap, 80mm slotted chrome plated union waste,
Aluminium brackets and other relevant accessories, pedestal
| crewed to the wall | 6 | nr |  | 0
D | Armitage Shanks ‘STREAMLINE’ shower tray Ref: 'L5542
| with anti slip resistant base. - Dimension: 800 x 800 x 160mm | 3 | nr |  | 0
E | Chrome plated towel rail size 600 x 13mm diameter | 4 | nr |  | 0
FIRE FIGHTING SYSTEMS
Supply, deliver to site and install the following items complete
with all necessary installation and operational accessories
F | Fe-ABC, 9Kg Class K, Amerex Model 2160 for Lab. installation | 5 | nr |  | 0
AIR CONDITIONING / EXTRACTORS / DUST
COLLECTORS
Equipment; Tropicalised extractor fan as manufactured by
Woods of Colchester Limited Xpelair, Vortice or other approved
G | Extractor fan | 4 | nr |  | 0
H | Inverter air conditioner with 9000 Btu capacity with
| both thermostattic and remote control Units | 5 | nr |  | 0
| PLUMBING AND MECHANICAL SERVICES CARRIED TO SUMMARY |  |  |  | 0
SUMMARY
1 | SUBSTRUCTURE |  |  |  | 0
2 | FRAMES |  |  |  | 0
3 | ROOF |  |  |  | 0
4 | INTERNAL AND EXTERNAL WALLS |  |  |  | 0
5 | WINDOWS |  |  |  | 0
6 | DOORS |  |  |  | 0
7 | FITTING AND FIXTURES |  |  |  | 0
8 | WALL FINISHES |  |  |  | 0
9 | CEILING FINISHES |  |  |  | 0
10 | FLOOR FINISHES |  |  |  | 0
11 | ELECTRICAL SERVICES |  |  |  | 0
12 | SOLAR POWER INSTALLATION |  |  |  | 0
13 | PLUMBING AND MECHANICAL SERVICES |  |  |  | 0
| CARRIED TO GENERAL SUMMARY |  |  |  | 0 | 0

## SUMMARY
BILL OF QUANTITIES FOR THE PROPOSED EXPANSION/MODIFICATION OF EXISTING PUBLIC HEALTH LABORATORY, AKURE ONDO STATE
GENERAL SUMMARY
S/No. | Name | No. | Amount (NGN) | Total Amount (NGN)
1 | Preliminaries and General Works | 1 | 0 | 0
2 | BOQ Laboratory Upgrade | 1 | 0 | 0
Total
TOTAL COST OF REXPANSION/MODIFICATION WORKS |  |  |  | 0